## Calculator
Cable Short-Circuit Withstand Calculator
Based on ICEA P-32-382 (phase) and ICEA P-45-482 (neutral/shield)
PHASE CONDUCTOR INPUTS |  |  | CONCENTRIC NEUTRAL INPUTS
Conductor material | Al | (Cu or Al) | Neutral wire count | 20 | wires
Conductor area | 211600 | cmil | Neutral wire size (AWG) | 12
T₁ — continuous operating temp | 90 | °C | T₁ — neutral operating temp | 90 | °C
T₂ — short-circuit max temp | 250 | °C | T₂ — neutral short-circuit max temp | 200 | °C
Fault clearing time | 30 | cycles | Ground-fault clearing time | 30 | cycles
Available phase fault current | 17 | kA | Ground-fault current on this neutral | 10 | kA
PHASE CONDUCTOR RESULTS |  |  | CONCENTRIC NEUTRAL RESULTS
K (material constant) | 0.0125 |  | Single wire area (from AWG table) | 6530 | cmil
λ (zero-resistance temp) | 228 | °C | Total neutral copper area | 130600 | cmil
Clearing time | 0.5 | seconds | Clearing time | 0.5 | seconds
Fc (short-circuit factor) | 0.047037 |  | Fc — neutral (copper) | 0.061402
Phase withstand current | 14.0758 | kA | Neutral withstand current | 11.3408 | kA
Maximum clearing time at given fault | 20.567 | cycles | Maximum clearing time at given fault | 38.5841 | cycles
PHASE VERDICT |  |  | NEUTRAL VERDICT
Phase withstand vs. available fault | FAIL |  | Neutral withstand vs. ground fault | PASS
Margin | -17.2% |  | Margin | 13.41%
NOTES
1. Blue values are inputs — change these for your project. Black values are calculated.
2. Phase withstand uses ICEA P-32-382. Neutral withstand uses ICEA P-45-482 basis (copper, reduced T₂).
3. Neutral T₂ is typically 180–200 °C (bare copper against jacket), not 250 °C. Confirm with manufacturer.
4. All currents are RMS symmetrical. Apply asymmetry factor to the fault side for high X/R.
5. The adiabatic model is conservative for clearing times beyond ~1–2 seconds.
6. Both checks must PASS for the cable to be acceptable.

## Reference
AWG | Area (cmil) | Insulation (T₁ → T₂) | Copper | Aluminum | Size | Copper (cmil) | Aluminum (cmil)
18 | 1620 | XLPE/EPR (90→250 °C) | 0.0719 | 0.047 | 1/0 AWG | 105600 | 105600
16 | 2580 | XLPE/EPR (105→250 °C) | 0.0678 | 0.0443 | 2/0 AWG | 133100 | 133100
14 | 4109 | PVC/PE (75→150 °C) | 0.0529 | 0.0346 | 3/0 AWG | 167800 | 167800
12 | 6530 |  |  |  | 4/0 AWG | 211600 | 211600
10 | 10380 | Insulation | T₁ (°C) | T₂ (°C) | 250 kcmil | 250000 | 250000
8 | 16510 | XLPE / TR-XLPE | 90 | 250 | 300 kcmil | 300000 | 300000
6 | 26240 | EPR | 90 | 250 | 350 kcmil | 350000 | 350000
4 | 41740 | PVC (≤300 mm²) | 75 | 160 | 500 kcmil | 500000 | 500000
2 | 66360 | PVC (larger) | 75 | 140 | 750 kcmil | 750000 | 750000
1 | 83690 | Paper / PILC | 85 | 250 | 1000 kcmil | 1000000 | 1000000
1/0 | 105600
|  | Standard | Scope
|  | ICEA P-32-382 | Short-circuit withstand of insulated conductors
|  | ICEA P-45-482 | Short-circuit performance of metallic shields & sheaths
|  | ICEA S-94-649 | Concentric-neutral cable construction, 5–46 kV
|  | IEEE 242 | Protection & coordination; cable damage curves
|  | IEC 60949 | International equivalent, with non-adiabatic correction